{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["sheet1"],"not_rendered":{"images":1,"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"sheet1","index":0,"n_rows":48,"n_cols":32,"rows_kept":48,"merged":[[2,1,5,9],[2,10,2,21],[2,22,2,33],[3,22,3,24],[3,25,3,27],[3,28,3,30],[3,31,3,33],[4,10,4,21],[4,22,4,24],[5,10,5,12],[5,22,5,24],[5,25,5,27],[5,28,5,33],[6,13,6,19],[6,20,6,26],[6,27,6,33],[7,1,8,12],[7,13,8,19],[7,20,8,26],[7,27,8,33],[9,13,9,19],[9,20,9,26],[9,27,9,33],[10,13,10,19],[10,20,10,26],[10,27,10,33],[12,13,12,19],[12,20,12,26],[12,27,12,33],[13,13,13,19],[13,20,13,26],[13,27,13,33],[14,13,14,19],[14,20,14,26],[14,27,14,33],[15,13,15,19],[15,20,15,26],[15,27,15,33],[16,13,16,19],[16,20,16,26],[16,27,16,33],[17,13,17,19],[17,20,17,26],[17,27,17,33],[19,13,19,19],[19,20,19,26],[19,27,19,33],[20,13,20,19],[20,20,20,26],[20,27,20,33],[21,13,21,19],[21,20,21,26],[21,27,21,33],[22,13,22,19],[22,20,22,26],[22,27,22,33],[23,13,23,19],[23,20,23,26],[23,27,23,33],[24,13,24,19],[24,20,24,26],[24,27,24,33],[25,13,25,19],[25,20,25,26],[25,27,25,33],[26,13,26,19],[26,20,26,26],[26,27,26,33],[27,13,27,19],[27,20,27,26],[27,27,27,33],[28,13,28,19],[28,20,28,26],[28,27,28,33],[29,13,29,19],[29,20,29,26],[29,27,29,33],[30,13,30,19],[30,20,30,26],[30,27,30,33],[31,13,31,19],[31,20,31,26],[31,27,31,33],[32,13,32,19],[32,20,32,26],[32,27,32,33],[33,13,33,19],[33,20,33,26],[33,27,33,33],[34,13,34,19],[34,20,34,26],[34,27,34,33],[35,13,35,19],[35,20,35,26],[35,27,35,33],[36,13,36,19],[36,20,36,26],[36,27,36,33],[37,13,37,19],[37,20,37,26],[37,27,37,33],[38,13,38,19],[38,20,38,26],[38,27,38,33],[39,13,39,19],[39,20,39,26],[39,27,39,33],[40,13,40,19],[41,13,41,19],[42,13,42,19],[42,20,42,26],[42,27,42,33],[43,1,43,12],[43,13,43,19],[43,20,43,26],[43,27,43,33],[44,13,45,19],[44,20,45,26],[44,27,45,33],[47,1,47,2],[47,3,47,9],[47,10,47,14],[47,15,47,17],[47,18,47,22],[47,23,47,25],[47,26,47,30],[47,31,47,33]],"flags":["formulas_cached_only"]}
[]
[]
[null,"                                                                                                     江苏索普工程科技有限公司          JiangSu SOPO Engineering Technology Co. Ltd.",{"$nulls":8},"仪表数据表                                                                                                  INSTRUMENT DATA SHEET",{"$nulls":11},"江苏索普（集团）有限公司                        醋酸造气工艺节能减排技术改造项目"]
[{"$nulls":10},"双法兰差压变送器",{"$nulls":11},"工程号\nENG. NO.",null,null,"201705",null,null,"主项号\nPROJ.NO.",null,null,23]
[{"$nulls":10},"D/P TRANSMITTER-LEVEL",{"$nulls":11},"图号\nDWG. NO.",{"$nulls":4},"201705-23K03-14/0"]
[{"$nulls":10},"合同号\nCONT. NO.",{"$nulls":11},"设计阶段\nSTAGE",null,null,"施工图",null,null,"第     1     张   共    3     张 \n SHEET    OF"]
[null,"位号 TAG NO.",{"$nulls":11},"PDT-1201"]
[null,"用途  SERVICE",{"$nulls":11},"气化炉/气化炉出口合成气压差指示，报警"]
[]
[null,"P&ID号 P&ID NO."]
[null,"设备位号 EQUIP.NO."]
[null,"操作条件 OPERATING CONDITIONS"]
[null,"工艺介质 PROCESS FLUID",{"$nulls":11},"合成气"]
[null,"操作压力 OPER.PRESS. MPa(G)",{"$nulls":11},"6.5"]
[null,"操作温度 OPER.TEMPER.℃",{"$nulls":11},"220～425"]
[null,"操作密度 DENSITY AT OPER. g/cm3"]
[null,"液位起始范围 INIT.LEVEL RAN. mm"]
[null,"法兰间距 FLANGE DISTAN. mm"]
[null,"变送器规格 TRANSMITTER SPECIFICATION"]
[null,"型号 MODEL"]
[null,"测量范围 MEAS.RANGE ",{"$nulls":11},"(0～400)kPa"]
[null,"精度 ACCURACY",{"$nulls":11},"±0.2%"]
[null,"输出信号 OUTPUT SIGNAL",{"$nulls":11},"4～20mA带HART"]
[null,"测量原理 MEAS.PRINCIPLE"]
[null,"测量元件材质 MEASURING ELEMENT MATERIAL",{"$nulls":11},"316L"]
[null,"本体材质 BODY MATERIAL",{"$nulls":11},"铝、覆聚氨酯涂层"]
[null,"终端接头规格 END CONN. SIZE",{"$nulls":11},"1/4\"NPT(F)"]
[null,"电气接口尺寸 ELEC.CONN.SIZE",{"$nulls":11},"1/2\"NPT(F)"]
[null,"防爆等级 EXPLOSION-PROOF CLASS",{"$nulls":11},"Exia II CT4"]
[null,"防护等级 ENCLOSURE PROOF",{"$nulls":11},"IP65"]
[null,"安装形式 INSTALLATION TYPE",{"$nulls":11},"2\" 法兰安装"]
[null,"隔离介质密度 DENS. OF SEAL MED. kg/m3"]
[null,"密封膜片材质 DIAPHRAGM MATERIAL",{"$nulls":11},"316L"]
[null,"法兰材质 FLANGE MATERIAL",{"$nulls":11},"316L"]
[null,"法兰标准及等级 FLANGE STD.& RATING",{"$nulls":11},"ANSI B16.5 900LB"]
[null,"法兰尺寸及密封面 FLANGE SIZE & FACING",{"$nulls":11},"2\"  RF"]
[null,"正负迁移范围  ELEVATION & SUPPRESSION"]
[null,"附件 ACCESSORIES",{"$nulls":11},"安装支架"]
[null,"输出指示表 OUTPUT INDICATOR",{"$nulls":11},"数字式表头"]
[null,"毛细管长度 CAPILLARY LENGTH",{"$nulls":11},"10米*2"]
[null,"毛细管材料 CAPILLARY MATERIAL",{"$nulls":11},"316L",{"$nulls":3},"316L"]
[null,"毛细管填充材料 CAP.FILL FLUID",{"$nulls":11},"高温硅油"]
[null,"制造厂 MANUFACTURER"]
[null,"数量  QUANTITY",{"$nulls":11},"1"]
[null,"备注  REMARKS",{"$nulls":11},"ROSEMOUNT/横河"]
[]
[{"$nulls":14},"  "]
[null,"修 改\nREV.",null,"说    明\nDESCRIPTION",{"$nulls":6},"设  计\nDESD",{"$nulls":4},"日 期\nDATE",null,null,"校  核\nCHED",{"$nulls":4},"日 期\nDATE",null,null,"审   核\nAPPD",{"$nulls":4},"日 期\nDATE"]