{"text_format":"3","workbook":"xlsx","n_sheets":1,"sheets":["sheet1"],"read":"whole","date_system":"1900"}

{"sheet":"sheet1","index":0,"n_rows":46,"n_cols":32,"rows_kept":46,"merged":[[2,1,5,9],[2,22,2,33],[3,22,3,24],[3,25,3,27],[3,28,3,30],[3,31,3,33],[4,22,4,24],[5,25,5,27],[9,1,9,4],[9,5,9,7],[9,8,9,10],[9,11,9,13],[9,14,9,19],[9,20,9,23],[9,24,9,28],[9,29,9,33],[10,29,10,33],[11,29,11,33],[12,29,12,33],[40,14,40,33],[41,14,41,33],[42,14,42,33],[45,1,45,2]]}
[]
[]
[]
[{"$nulls":10},"热电偶",{"$nulls":11},"工程号\nENG. NO.",null,null,"201329",null,null,"主项号\nPROJ.NO.",null,null,"01"]
[{"$nulls":10},"THERMOCOUPLE",{"$nulls":11},"图号\nDWG. NO.",{"$nulls":4},"201329-01K03-03/0"]
[{"$nulls":25},"施工图"]
[{"$nulls":5},"操作条件 OPERATING CONDITIONS",{"$nulls":8},"长度 LENGTH(mm)"]
[null,"位号 ",{"$nulls":3},"工艺介质 ",null,null,"压力MPa G",null,null,"温度 ℃",null,null,"全长/插入深度 (mm)",{"$nulls":5},"刻度范围 ℃ ",{"$nulls":3},"P&ID号",{"$nulls":4},"备注"]
[null,"TAG NO.",{"$nulls":3},"FLUID",null,null,"PRESSURE",null,null,"TEMP.",null,null,"OVERALL/INSER.LENG.",{"$nulls":5},"SCALE",{"$nulls":3},"P&ID NO.",{"$nulls":4},"REMARKS"]
[null,"TE-045",{"$nulls":3},"燃料气",null,null,"0.055",null,null,"1019",null,null,"750/500",{"$nulls":5},"0-1600",{"$nulls":3},"201329-01P03-06",{"$nulls":4},"1支"]
[null,"TE/TT-008",{"$nulls":3},"过程气",null,null,"0.055",null,null,"1019",null,null,"870/620",{"$nulls":5},"0-1600",{"$nulls":3},"201329-01P03-06",{"$nulls":4},"1支"]
[null,"TE/TT-009",{"$nulls":3},"过程气",null,null,"0.055",null,null,"1019",null,null,"870/620",{"$nulls":5},"0-1600",{"$nulls":3},"201329-01P03-06",{"$nulls":4},"1支"]
[null,"TE/TT-010",{"$nulls":3},"过程气",null,null,"0.055",null,null,"1019",null,null,"870/620",{"$nulls":5},"0-1600",{"$nulls":3},"201329-01P03-06",{"$nulls":4},"1支"]
{"$rows_empty":9}
[null,"热电偶规格 THERMOCOUPLE SPECIFICATION"]
[null,"型号 MODEL",{"$nulls":13},"SBWRP-4452"]
[null,"分度号 MARK GRADUATION",{"$nulls":13},"S"]
[null,"测温元件数量 THERMO ELEMENT QNTY.",{"$nulls":13},"1"]
[null,"热电偶材料 THERMOCOUPLE MATERIAL",{"$nulls":13},"铂铑10-铂"]
[null,"结构形式 CONSTRUCTION STYLE",{"$nulls":13},"铠装"]
[null,"测温端形式 HOT JUNCTION STYLE"]
[null,"保护管直径 THERMOWELL DIAMETER (mm)",{"$nulls":13},"Φ8"]
[null,"精度 ACCURACY ",{"$nulls":13},"±0.5%"]
[null,"输出信号 OUTPUT SIGNAL",{"$nulls":13},"4～20mA带Hart"]
[null,"电源 POWER SUPPLY",{"$nulls":13},"24VDC"]
[null,"接线盒防护等级 ENCLOSURE PROOF",{"$nulls":13},"IP65"]
[null,"防爆等级 EXPLOSION-PROOF CLASS",{"$nulls":13},"ExiaIICT4"]
[null,"安装固定方式 MOUNTING STYLE",{"$nulls":13},"法兰连接"]
[null,"法兰标准及等级 FLANGE STD.& RATING",{"$nulls":13},"ANSI B16.5 150lb"]
[null,"法兰尺寸及密封面 FLANGE SIZE & FACING",{"$nulls":13},"2\" WN RF"]
[null,"电气接口尺寸 ELEC.CONN.SIZE",{"$nulls":13},"M20X1.5"]
[null,"制造厂 MANUFACTURER"]
[{"$nulls":14},"带温度变送器：罗斯蒙特、WIKA、ABB、E+H"]
[{"$nulls":14},"套管材质：刚玉 ，套管直径：Φ30+涂层"]
[{"$nulls":14},"热偶丝必须要达到测量点头部"]
[{"$nulls":5},"制硫炉"]
[{"$nulls":14},"  "]
[null,"修 改\nREV."]