{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["Sheet1","Sheet2"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":43,"n_cols":31,"rows_kept":43,"merged":[[0,0,3,8],[0,9,0,20],[0,21,0,32],[1,21,1,23],[1,24,1,26],[1,27,1,29],[1,30,1,32],[2,9,2,20],[2,21,2,23],[3,9,3,11],[3,21,3,23],[3,24,3,26],[3,27,3,32],[4,13,4,17],[4,18,4,27],[4,28,4,32],[5,0,6,12],[5,13,6,17],[5,18,5,27],[5,28,5,32],[6,28,6,32],[7,13,7,17],[7,28,7,32],[8,13,8,17],[8,28,8,32],[9,13,9,17],[9,28,9,32],[10,13,10,17],[11,28,11,32],[12,13,12,17],[12,28,12,32],[13,13,13,17],[13,28,13,32],[14,13,14,17],[14,28,14,32],[15,13,15,17],[15,28,15,32],[16,28,16,32],[17,0,19,2],[17,13,17,17],[17,28,17,32],[18,13,18,17],[18,28,18,32],[19,13,19,17],[19,18,19,32],[20,13,20,17],[20,28,20,32],[21,13,21,17],[21,28,21,32],[22,13,22,17],[22,28,22,32],[23,28,23,32],[24,13,24,17],[24,28,24,32],[25,13,25,17],[25,28,25,32],[26,28,26,32],[27,13,27,17],[27,28,27,32],[28,28,28,32],[29,13,29,17],[30,13,30,17],[30,28,30,32],[31,13,31,17],[31,28,31,32],[32,13,32,17],[32,28,32,32],[33,13,33,17],[33,28,33,32],[34,13,34,17],[34,28,34,32],[35,13,35,17],[35,18,36,27],[35,28,36,32],[36,13,36,17],[37,13,37,17],[37,18,39,32],[38,13,38,17],[39,13,39,17],[40,10,40,12],[41,10,41,12],[42,0,42,1],[42,2,42,8],[42,9,42,13],[42,14,42,16],[42,17,42,21],[42,22,42,24],[42,25,42,29],[42,30,42,32]],"flags":["formulas_cached_only"]}
[{"$nulls":9},"仪表数据表                                                                                                  INSTRUMENT DATA SHEET"]
[{"$nulls":9},"调节阀",{"$nulls":11},"工程号\nENG. NO.",{"$nulls":5},"主项号\nPROJ.NO."]
[{"$nulls":9},"CONTROL VALVE",{"$nulls":11},"图号\nDWG. NO."]
[{"$nulls":9},"合同号\nCONT. NO.",{"$nulls":11},"设计阶段\nSTAGE",null,null,"施工图"]
["位号 TAG NO.",{"$nulls":12},"FV-1408",{"$nulls":4},"计算 Cv  CALC.Cv"]
["用途  SERVICE",{"$nulls":12},"P1406A/B进口\n稀酸流量调节",{"$nulls":4},"选择 Cv  RATED Cv"]
[{"$nulls":18},"连接形式 CONNECTION TYPE",{"$nulls":9},"法兰连接"]
["P&ID号 P&ID NO.",{"$nulls":17},"法兰标准及等级FLANGE STD.&DEGREE",{"$nulls":9},"ANSI B16.5"]
["管道编号 LINE NO.",{"$nulls":17},"法兰尺寸及密封面",{"$nulls":4}," FLANGE SIZE&SEAL.",{"$nulls":4},"2\"-300LB RF"]
["管道材质 PIPE MATERIAL",{"$nulls":17},"法兰材质 FLANGE MATERIAL",{"$nulls":9},"Zr702"]
["管道规格 PIPE SPECIFICATION",{"$nulls":17}," 执行机构 ACTUATOR"]
["操作条件 OPERATING CONDITIONS",{"$nulls":17},"型号 MODEL",{"$nulls":9},"——"]
["工艺介质 PROCESS FLUID",{"$nulls":12},"稀酸",{"$nulls":4},"型式 TYPE",{"$nulls":9},"弹簧薄膜"]
["操作温度 OPER. TEMPER.℃",{"$nulls":12},"70",{"$nulls":4},"作用形式 ACTION"]
["阀前压力 UPSTREAM PRESSURE MPa(A)",{"$nulls":12},"4.3",{"$nulls":4},"弹簧范围 SPRING RANGE",{"$nulls":9},"0.08~0.24MPa"]
["阀后压力 DOWNSTREAM PRESSURE MPa(A)",{"$nulls":12},"2.8",{"$nulls":4},"相对行程 TRAVEL",{"$nulls":9},"——"]
["阀关闭差压 SHUT-OFF DIFF.PRESSURE MPa",{"$nulls":17},"手轮 HAND WHEEL",{"$nulls":9},"——"]
["流量                FLOW",null,null,"气体 GAS Nm3/h",{"$nulls":6},"最大 MAX.",null,null,"8",{"$nulls":4},"供气压力 AIR SUPPLY PRESS.",{"$nulls":9},"0.25MPa"]
[{"$nulls":3},"蒸汽 VAPOR Kg/h",{"$nulls":6},"正常 NOR.",null,null,"5",{"$nulls":4},"气源接头 AIR CONN.SIZE",{"$nulls":9},"1/4\"NPT"]
[{"$nulls":3},"液体 LIQUID m3/h",{"$nulls":6},"最小 MIN.",{"$nulls":7},"电气定位器 I/P POSITIONER"]
["操作密度 OPER. DENSITY Kg/m3 　",{"$nulls":12},"1009",{"$nulls":4},"型号 MODEL",{"$nulls":9},"见备注"]
["动力粘度 DYNAMIC VISCOSITY mPa.s",{"$nulls":17},"输入信号 INPUT SIGNAL",{"$nulls":9},"4~20mA带HART"]
["比重(空气=1)SPEC.GRAV.(AIR=1)",{"$nulls":17},"输出信号 OUTPUT SIGNAL",{"$nulls":9},"0.02~0.1MPa"]
["压缩系数 COMPRESS FACTOR K",{"$nulls":17},"气源压力 AIR SUPPLY PRESS.",{"$nulls":9},"0.14~0.5MPa"]
["气化压力 VAPOR PRESSURE MPa Pv ",{"$nulls":17},"作用形式 ACTION",{"$nulls":9},"——"]
["临界压力 CRITICAL PRESSURE MPa Pc",{"$nulls":17},"电气接口尺寸 ELEC.CONN.SIZE",{"$nulls":9},"1/2\"NPT"]
["噪音声平 NOISE LEVEL",{"$nulls":17},"气信号接口尺寸 PNEU.CONN.SIZE",{"$nulls":9},"1/4\"NPT"]
["空气故障时阀位置  AIR FAIL VALVE POSITION",{"$nulls":12},"关闭",{"$nulls":4},"气源接口尺寸 AIR SUPP.CONN.SIZE",{"$nulls":9},"1/4\"NPT"]
["阀体/阀芯规格 BODY/PLUG SPECIFICATION",{"$nulls":17},"防爆等级 EXPLOSION-PROOF CLASS",{"$nulls":9},"ExdIIBT4"]
["阀型号 VALVE MODEL",{"$nulls":17},"附件 ACCESSORY"]
["阀型式 VALVE TYPE",{"$nulls":12},"套筒",{"$nulls":4},"过滤器减压阀 REGULATOR",{"$nulls":9},"带"]
["流开/流关 FLOW OPEN/CLOSE",{"$nulls":17},"阀位反馈 POSITION SWITH",{"$nulls":9},"——"]
["阀座数量 NO. OF SEATS",{"$nulls":12},"1",{"$nulls":4},"电磁阀 SOLENOID",{"$nulls":9},"ASCO WSNF8327B202"]
["阀芯型式 PLUG TYPE",{"$nulls":12},"压力平衡式",{"$nulls":4},"法兰间距不含RF面 DISTANCE (mm)",{"$nulls":9},"295"]
["阀口径 PORT SIZE/阀座",{"$nulls":12},"2\"",{"$nulls":4},"数量  QUANTITY",{"$nulls":9},"1"]
["流量特性 FLOW CHARACTERISTIC",{"$nulls":12},"等百分比",{"$nulls":4},"备注  REMARKS",{"$nulls":9},"泄漏等级 V级"]
["散热片/延伸杆 FIN/EXTENTION"]
["阀体材质 BODY MATERIAL",{"$nulls":12},"Zr702",{"$nulls":4},"\n1.阀门定位器品牌FISHER DVC6200、福斯 3200MD或萨姆森3731\n"]
["阀芯材质 PLUG MATERIAL",{"$nulls":12},"Zr702"]
["阀座材质 SEAT MATERIAL",{"$nulls":12},"Zr702"]
[]
[{"$nulls":13},"  "]
["修 改\nREV.",null,"说    明\nDESCRIPTION",{"$nulls":6},"设  计\nDESD",{"$nulls":4},"日 期\nDATE",null,null,"校  核\nCHED",{"$nulls":4},"日 期\nDATE",null,null,"审   核\nAPPD",{"$nulls":4},"日 期\nDATE"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}